Ahsanullah University of Science and Technology

Topic:

Overload detection and protection system

Course No: EEE 4154

Course Name: Power System II Lab

Submitted by: Group 2

Group Members:

20220105084
20220105076
20220105060
20200205083
20220105063

Section: B1

Year: 4th

Semester: 1st

Department: EEE

Objective

In modern electrical systems, protection mechanisms are essential to ensure safe, reliable, and efficient operation. One of the most common abnormal operating conditions is overload, where the current drawn by a load exceeds its rated capacity.

Overload results in excessive heat generation due to I²R losses, leading to insulation degradation, reduced efficiency, and possible equipment failure.

This project presents an overload detection and protection system that continuously monitors load current using an ACS712 Current sensor. When the measured current exceeds a predefined threshold, the system isolates the load through relays, activates an audible alarm, and displays system status on an i2c LCD display. The system demonstrates a practical implementation of overcurrent protection in low-voltage applications.

Component Description

- ACS712 Current sensor
Hall-effect based sensor used to measure load current and provide an analog output proportional to current.

- Arduino UNO
Used for signal processing, current evaluation, and control of relay, buzzer, and display.

- Relay
Electromagnetic switching device used to isolate the load during overload condition and provide electrical isolation.

- buzzer
Provides audible indication during fault condition.

- i2c LCD display
Displays real-time current value and system status.

- Transformer
Steps down AC voltage from mains to a safe low-voltage level.

- 1N4007
Rectifier diode used to convert AC to pulsating DC.

- Capacitor
Filters the rectified DC voltage and reduces ripple.

- 7805 voltage regulator
Provides regulated 5V DC supply.

- R1
Current limiting resistor for LED protection.

- led
Indicates power availability.

- Switch
Used for manual control of relays during normal operation.

- BULB
Represents the electrical load connected to the system.

Circuit Diagram

Figure: Circuit diagram of overload detection and protection system

Working Principle

The system continuously monitors load current and performs protective action when the current exceeds a safe limit.

Power Supply Stage

The transformer steps down AC voltage. The 1N4007 diode rectifies the AC signal, the capacitor smooths the output, and the 7805 regulator provides a stable 5V DC supply.

Sensing Stage

The ACS712 Current sensor is connected in series with the BULB. It generates an analog voltage proportional to the load current.

Signal Processing Stage

The analog signal is read and converted into digital form. The current is calculated based on sensor calibration.

Overload Detection

The threshold current is set to 700 mA. When the measured current exceeds this value, an overload condition is detected.

Protective Action

During overload condition, both relays are deactivated to isolate the load. The buzzer is activated and the LCD displays a fault message. The system enters a latched fault state.

Normal Operation

When the current is within safe limits, the system operates normally. The LCD displays the current value and system status, and the switches allow manual control of relays.

Mathematical Analysis

The load current can be estimated using:

I = P / V

For a 100 W bulb operating at 220 V:

I = 100 / 220 = 0.45 A

For two identical bulbs:

I = 200 / 220 = 0.91 A

Since the system threshold is 0.7 A:

- One bulb operates under normal condition

- Two bulbs exceed the threshold and trigger overload protection

Experimental Results

| Condition | Load Power (W) | Calculated Current (A) | Measured Current (A) | System Status |
| --- | --- | --- | --- | --- |
| No load | 0 | 0.00 | 0.02 | Normal |
| 1 bulb | 100 | 0.45 | 0.43 | Normal |
| 2 bulbs | 200 | 0.91 | 0.88 | Fault Detected |

Protection Concept

The system implements a basic overcurrent protection scheme for low-voltage loads. When the load current exceeds a predefined threshold, the relay isolates the circuit, preventing thermal damage.

The protection mechanism includes:

- Definite threshold overcurrent protection

- Instantaneous tripping

- Manual restoration after fault

Advantages

- Provides effective overload protection

- Ensures fast fault detection and isolation

- Simple, low-cost, and easy to implement

- Provides real-time monitoring

- Improves system safety and reliability

Limitations

- Limited current range based on sensor rating

- Cannot detect short-circuit faults

- No time-delay protection implemented

- Fault reset is not automated

- Measurement accuracy depends on sensor calibration

Conclusion

This project successfully demonstrates an overload detection and protection system for low-voltage applications. By continuously monitoring current and isolating the load during overcurrent conditions, the system prevents equipment damage and enhances operational safety.

Future Improvements

- Implementation of time-delay overcurrent protection

- Addition of automatic reset mechanism

- Integration with IoT for remote monitoring

- Data logging for system analysis

- Implementation of inverse-time protection characteristics

- Addition of voltage and power factor measurement